## OF Master List
OF ID | OF Location | Catchment Priority | Catchment Investigation Status | Date Visited | T&B Field Inspector | # of KJMHs in Catchment | # of KJMHs Visited | All KJMHs Complete? | Other non-KJMH structures visited? | System Mapping Updates Needed? | Field Notes/Questions | Suspected IDDE? | GIS QC? | GIS QC Notes | PM Notes | Wet Weather Needed at this Outfall? | Wet Weather Status | Date Visited | T&B Field Inspector | Reason to Investigate (SVF) | Sampling Results Summarized (individual results to be in separate tab)
[8 empty] | Yes/No |  |  |  |  | Yes/No |  |  | Yes/No
OF_181 | Preservation way | Low | Visited - Complete | 2021-10-07 13:00 | S. Downes | 1 | 1 | Yes | Yes | No | Flow from culvert into CB4392. None from street. Confirmed network | Unlikely |  |  |  | No | - | - | - | - | -
UNK-35 | Woodbury Drive | Low | Visited - Complete | 2021-10-07 13:18 | S. Downes | 1 | 1 | Yes | Yes | No | Confirmed network | Unlikely |  |  |  | No | - | - | - | - | -
OF_193 | Snow Drive | Low | Visited - Complete | 2021-10-07 13:30 | S. Downes | 1 | 1 | Yes | Yes | No | Confirmed network | Unlikely |  |  |  | No | - | - | - | - | -
OF_19 | Whitney Drive | Low | Visited - Complete | 2021-10-07 | S. Downes | 0 | 0 | Yes | Yes | Yes | Update network to show new pipe connections. | Unlikely |  |  |  | No | - | - | - | - | -
OF_20 | Fieldstone Drive | Low | Revisit | 2021-10-07 | S. Downes | 0 | 0 | Yes | Yes | Yes | Update network. | Unlikely |  |  |  | No | - | - | - | - | -
New_AA | Melissa Drive | Low | Visited - Complete | 2021-10-07 | S. Downes | 0 | 0 | Yes | Yes | Yes | Update network. | Unlikely |  |  |  | No | - | - | - | - | -
-* | Steeple Chase Circle | NA | Revisit | 2021-10-07 14:20 | S. Downes | 1 | 1 | Yes | Yes | Yes | Update network. | Unlikely |  |  |  | No | - | - | - | - | -
UNK-7 | Steeple Chase Circle | Low | Revisit | 2021-10-07 14:26 | S. Downes | 1 | 1 | Yes | Yes | Yes | Update mapping to show pipe from 4107 | Unlikely |  |  |  | No | - | - | - | - | -
UNK-61 | Fieldstone Drive | Low | Visited - Complete | 2021-10-07 15:05 | S. Downes | 1 | 1 | Yes | Yes | No | Confirmed network | Unlikely |  |  |  | No | - | - | - | - | -
OF_298 | Fairview Drive | Low | Visited - Complete | 2021-10-07 15:33 | S. Downes | 1 | 1 | Yes | Yes | No | Confirmed network | Unlikely |  |  |  | No | - | - | - | - | -
OF_293 | Tadmuck Lane | Low | Visited - Complete | 2021-10-07 15:42 | S. Downes | 1 | 1 | Yes | Yes | No | Confirmed network; flow from 2931. Flow from 2932 | Unlikely |  |  |  | No | - | - | - | - | -
OF_292 | Fairview Drive | Low | Visited - Complete | 2021-10-07 | S. Downes | 1 | 1 | Yes | Yes | Yes | Update network. | Unlikely |  |  |  | No | - | - | - | - | -
OF_290 | Kersi Circle | Low | Revisit | 2021-10-07 | S. Downes | 2 | 2 | No | Yes | Yes | Update network | Unlikely |  |  |  | No | - | - | - | - | -
OF_286 | Kirsi Circle | High | Visited - Complete | 2021-10-07 | S. Downes | 1 | 1 | Yes | Yes | Yes | Update network. | Unlikely |  |  |  | No | - | - | - | - | -
OF_288 | Douglas Road | Low | Visited - Complete | 2021-10-07 | S. Downes | 1 | 1 | Yes | Yes | Yes | Update mapping for new construction. | Unlikely |  |  |  | No | - | - | - | - | -
OF_1048 | Moore Rd | Low | Visited - Complete | 2021-12-15 | E.Balcom | 1 | 1 | Yes | No | No | Confirmed network | Unlikely |  |  |  | No | - | - | - | - | -
OF_1049 | Lucille Avenue | Low | Visited - Complete | 2021-12-15 | E.Balcom | 1 | 1 | Yes | No | No | Confirmed network | Unlikely |  |  |  | No | - | - | - | - | -
OF_1032 | Brookside Rd | Low | Visited - Complete | 2021-12-15 | E.Balcom | 1 | 1 | Yes | No | No | Confirmed network | Unlikely |  |  |  | No | - | - | - | - | -
OF_164 | Hadley Rd | Low | Visited - Complete | 2021-12-15 | E.Balcom | 1 | 1 | Yes | No | No | Confirmed network | Unlikely |  |  |  | No | - | - | - | - | -
OF_1037 | Pine Tree Trail | Low | Visited - Complete | 2021-12-15 | E.Balcom | 1 | 1 | Yes | No | No | Confirmed network | Unlikely |  |  |  | No | - | - | - | - | -
UNK-37 | Fernwood Dr | Low | Visited - Complete | 2021-12-15 | E.Balcom | 1 | 1 | Yes | No | No | Confirmed network | Unlikely |  |  |  | No | - | - | - | - | -
OF_1026 | Kayla Dr | Low | Visited - Complete | 2021-12-15 | E.Balcom | 1 | 1 | Yes | No | No | Confirmed network | Unlikely |  |  |  | No | - | - | - | - | -
OF_459 | Lindsey Lane | Low | Visited - Complete | 2021-12-15 | S. Downes | 1 | 1 | Yes | No | No | Confirmed in other manholes | Unlikely |  |  |  | No | - | - | - | - | -
OF_382 | Lynnwood Lane | Low | Visited - Complete | 2021-12-15 | S. Downes | 1 | 1 | Yes | No | No | Confirmed network | Unlikely |  |  |  | No | - | - | - | - | -
OF_540 | Lakeside Terrace | Low | Visited - Complete | 2021-12-15 | S. Downes | 1 | 1 | Yes | No | No | Confirmed network | Unlikely |  |  |  | No | - | - | - | - | -
OF_538 | Lakeside Terrace | Low | Visited - Complete | 2021-12-15 | S. Downes | 1 | 1 | Yes | No | No | Confirmed network | Unlikely |  |  |  | No | - | - | - | - | -
OF_533 | Birchwood Drive | Low | Visited - Complete | 2021-12-15 | S. Downes | 1 | 1 | Yes | No | No | Confirmed network | Unlikely |  |  |  | No | - | - | - | - | -
Notes:
*Unmapped OF. KJMH 5533

## KJMH inspections
Catchment Outfall ID | KJMH # in Catchment | KJMH ID (Asset ID) |  | KJMH Location | Date Visited | Investigators | Temperature (F) | Rainfall (In) Last 72 Hours | Rainfall (In) Last 24 Hours | Maintenance Needs | Other - Maintenance Needs | Inverts Submerged? | If yes, which pipe? | Flow Present? | # Samples Taken at KJMH (add additional rows if >1) | Evidence of Potential Illicit Connection? | Flow Description | Flow Source | Intermittent flow trap (e.g., sandbag recommended) recommended? | Surfactants (mg/L) | Ammonia (mg/L) | Chlorine (mg/L) | Odor | Odor Description | Other - Odor Description | Floatables (Does Not Include Trash) | Floatables Description | Other - Floatables Description | Notes | insp_type
(street)
OF_181 | 1 | 5588 | MH | Preservation way | 2021-10-07 13:00 | S. Downes | 55 | 1.6 | 0.0 |  |  | No |  | No | - | - |  |  |  | - | - | - | No |  |  | No |  |  | -
UNK-35 | 1 | 4411 | MH | Woodbury Drive | 2021-10-07 13:00 | S. Downes | 55 | 1.6 | 0.0 |  |  | No |  | No | - | - |  |  |  | - | - | - | No |  |  | No |  |  | -
OF_193 | 1 | 4421 | CB | Snow Drive | 2021-10-07 13:00 | S. Downes | 55 | 1.6 | 0.0 |  |  | No |  | No | - | - |  |  |  | - | - | - | No |  |  | No |  |  | -
OF_19 | 0 | - |  | Whitney Drive | 2021-10-07 13:00 | S. Downes | [7 empty] | No | [14 empty] | -
OF_20 | 0 | - |  | Fieldstone Drive | 2021-10-07 13:00 | S. Downes | [7 empty] | No
New_AA | 0 | - |  | Melissa Drive | 2021-10-07 13:00 | S. Downes | [7 empty] | No
-* | 1 | 5533 | MH | Steeple Chase Circle | 2021-10-07 13:00 | S. Downes | 60 | 1.6 | 0.0 |  |  | No |  | No | - | - |  |  |  | - | - | - | No |  |  | No |  |  | -
UNK-7 | 1 | 5527 | MH | Steeple Chase Circle | 2021-10-07 13:00 | S. Downes | 55 | 1.6 | 0.0 |  |  | No |  | No | - | - |  |  |  | - | - | - | No |  |  | No |  |  | -
UNK-61 | 1 | 864 | MH | Fieldstone Drive | 2021-10-07 13:00 | S. Downes | 65 | 1.6 | 0.0 | other | Paved over. Checked upstream and downstream manholes. All dry. | No |  | No | - | - |  |  |  | - | - | - | No |  |  | No |  |  | -
OF_298 | 1 | 2913 | CB | Fairview Drive | 2021-10-07 13:00 | S. Downes | 65 | 1.6 | 0.0 |  |  | No |  | No | - | - |  |  |  | - | - | - | No |  |  | No |  |  | -
OF_293 | 1 | 2930 | CB | Tadmuck Lane | 2021-10-07 13:00 | S. Downes | 65 | 1.6 | 0.0 |  |  | No |  | Yes | 1 of 2 | No | Trickle | Both directions. Sample results indicated in notes. | No | 0.25 | 0.0 | 0.11 | No |  |  | No |  |  | Flow from 2931
OF_293 | 1 | 2930 |  | Tadmuck Lane | 2021-10-07 | S. Downes | [7 empty] | Yes | 2 of 2 | No |  |  |  | 0.25 | 0 | 0.05 | [6 empty] | Flow from 2932
OF_292 | 1 | 2938 | CB | Fairview Drive | 2021-10-07 13:00 | S. Downes | 65 | 1.6 | 0.0 |  |  | Partially | Both. | Yes | 1 | No | Trickle | From down street towards MH | No | 0.0 | 0.0 | 0.04 | No |  |  | No |  |  | - | Dry Key Junction
OF_290 | 2 | KirsiMH290; 2884 | MH | Kersi Circle | 2021-10-07 13:00 | S. Downes | 70 | 1.6 | 0.0 |  |  | No |  | No | - | - |  |  |  | - | - | - | No |  |  | No |  |  | - | Dry Key Junction
OF_288 | 1 | 2907 | MH | Douglas Road | 2021-10-07 13:00 | S. Downes | 70 | 1.6 | 0 |  |  | No |  | No | - | - |  |  |  | - | - | - | No |  |  | No |  |  | - | Dry Key Junction
OF_286 | 1 | 2901 | CB | Kirsi Circle | 2021-10-07 13:00 | S. Downes | 75 | 1.6 | 0.0 |  |  | No |  | No | - | - |  |  |  | - | - | - | No |  |  | No |  |  | - | Dry Key Junction
OF_1048 | 1 | 1653 | MH | Moore Rd | 2021-12-15 14:01 | E. Balcom | 34 | 0 | 0 |  |  | No |  | No | - | - |  |  |  | - | - | - | No |  |  | No |  |  | - | Dry Key Junction
OF_1049 | 1 | 1345 | MH | Lucille Avenue | 2021-12-15 14:01 | E. Balcom | 30 | 0 | 0 |  |  | No |  | No | - | - |  |  |  | - | - | - | No |  |  | No |  |  | - | Dry Key Junction
OF_1032 | 1 | 1623 | MH | Brookside Rd | 2021-12-15 14:01 | E. Balcom | 30 | 0 | 0 |  |  | No |  | No | - | - |  |  |  | - | - | - | No |  |  | No |  |  | - | Dry Key Junction
OF_164 | 1 | 1622 | MH | Hadley Rd | 2021-12-15 14:01 | E. Balcom | 34 | 0 | 0 | other | Sediment in bottom | No |  | No | - | - |  |  |  | - | - | - | No |  |  | No |  |  | - | Dry Key Junction
OF_1037 | 1 | 1407 | MH | Pine Tree Trail | 2021-12-15 14:01 | E. Balcom | 34 | 0 | 0 |  |  | No |  | No | - | - |  |  |  | - | - | - | No |  |  | No |  |  | - | Dry Key Junction
UNK-37 | 1 | 1703 | MH | Fernwood Dr | 2021-12-15 14:01 | E. Balcom | 34 | 0 | 0 |  |  | No |  | No | - | - |  |  |  | - | - | - | No |  |  | No |  |  | - | Dry Key Junction
OF_1026 | 1 | 1546 | MH | Kayla Dr | 2021-12-15 14:01 | E. Balcom | 36 | 0 | 0 |  |  | No |  | No | - | - |  |  |  | - | - | - | No |  |  | No |  |  | - | Dry Key Junction
OF_459 | 1 | 2391 | MH | Lindsey Lane | 2021-12-15 14:01 | S. Downes | 40 | 0 | 0 |  |  | No |  | No | - | - |  |  |  | - | - | - | No |  |  | No |  |  | - | Dry Key Junction
OF_382 | 1 | 2395 | MH | Lynnwood Lane | 2021-12-15 14:01 | S. Downes | 35 | 0 | 0 |  |  | No |  | No | - | - |  |  |  | - | - | - | No |  |  | No |  |  | - | Dry Key Junction
OF_540 | 1 | 3974 | MH | Lakeside Terrace | 2021-12-15 14:01 | S. Downes | 35 | 0 | 0 |  |  | Partially | All pipes. Confirmed no flow at outfall and upstream, structures. | No | - | - |  |  |  | - | - | - | No |  |  | No |  |  | - | Dry Key Junction
OF_538 | 1 | 3950 | MH | Lakeside Terrace | 2021-12-15 14:01 | S. Downes | 35 | 0 | 0 |  |  | No |  | No | - | - |  |  |  | - | - | - | No |  |  | No |  |  | - | Dry Key Junction
OF_533 | 1 | 3959 | MH | Birchwood Drive | 2021-12-15 14:01 | S. Downes | 35 | 0 | 0 |  |  | No |  | No | - | - |  |  |  | - | - | - | No |  |  | No |  |  | - | Dry Key Junction
Notes:
*Unmapped OF. KJMH 5533

## Wet Weather Sampling
2022 Wet Weather Outfall Sampling Results Summary - Westford, MA
Location |  |  |  |  | Laboratory Analysis (1) |  |  |  |  | Water Quality Meter/Test Kit (1)
Date | Time | Outfall ID | Street | Sample Location | Ammonia | Surfactants | E. coli | Total Phosphorus | Temperature | Temperature | Salinity | Conductivity | Chlorine | Ammonia | Dissolved Oxygen
[5 empty] | mg/L | mg/L | CFU/100mL | mg/L | oC | oF | ppt | µS/cm (2) | mg/L | mg/L | mg/L
No outfalls were visited that required wet weather screening.
REPORTING LIMITS Ammonia = 0.075 mg/L Surfactants = 0.050 mg/L E. coli = 2 CFU/100mL Fecal Coliform = 2 CFU/100mL BOD5 = 2 mg/L Total Phosphorus = 0.01 mg/L "ND" = none detected |  |  |  | COLOR KEY (benchmarks are bold)
[5 empty] | Ammonia | Surfactants | E. coli | Total Phosphorus |  | Temperature | Salinity | Conductivity | Chlorine | Ammonia | Dissolved Oxygen
[5 empty] | mg/L | mg/L | CFU/100 mL | mg/L |  | oF | ppt | µS/cm | mg/L | mg/L | mg/L
[5 empty] | 6 | 1 | 10000 | 0.908 |  | 83 | 1 | 2000 | 1 | 6
[5 empty] | 1 | 0.5 | 1260 | 0.466 |  | 83 | 0.75 | 1500 | 0.3 | 1
[5 empty] | 0.5 | 0.25 | 235 | 0.024 |  | 83 | 0.5 | 1000 | 0.02 | 0.5 | 5
[5 empty] | < 0.5 | < 0.25 | < 235 | < 0.024 |  | < 83 | < 0.5 | < 1,000 | < 0.02 | < 0.5 | ≥ 5.0
Notes for Results Summary: |  |  |  | Benchmark Sources:
(1) "-" means no analysis was completed |  |  |  | Ammonia, Surfactants, and Chlorine - EPA General Permit for Stormwater Discharges from Small MS4 in Massachusetts
(2) µS/cm is equivalent to µmhos/cm |  |  |  | E. coli, Temperature, and Dissolved Oxygen - 314 CMR 4.00: Massachusetts Surface Water Quality Standards
(3) analytical method 121,9213D |  |  |  | Fecal coliform - MWRA Water Quality Standards for Class B and Class SB Waters
Total Phosphorus - EPA Ambient Water Quality Criteria Recommendations for Rivers and Streams in Nutrient Ecoregion XIV
Salinity - EPA Volunteer Estuary Monitoring: A Methods Manual
Conductivity - Center for Watershed Protection Illicit discharge Detection and Elimination Guidance Manual
BOD5 has no quantitative benchmark for surface water grab samples

## Totals (hidden)
Catchment Investigation Status | Count | %
Visited - Complete | 23 | 85.1852
Revisit | 4 | 14.8148
Not Applicable | 0 | 0
Not Visited | 0 | 0
Total # of OF Catchments: | 27

## Superseded KJMH in-situ results (hidden)
Catchment Outfall ID | Key Junction Structure ID | Structure Type | Structure Location | Todays Date/Time | Investigators | Temperature (F) | Rainfall (In) Last 72 Hours | Rainfall (In) Last 24 Hours | Maintenance Needs | Other - Maintenance Needs | Inverts Submerged? | If yes, which pipe? | Flow Present? | Flow Description | Flow Source | Intermittent flow trap (e.g., sandbag recommended) recommended? | Surfactants (>0.25 mg/L) Result | Ammonia (NH3)(>0.5 mg/L) Result | Chlorine (>0.02 mg/L) Result | Odor | Odor Description | Other - Odor Description | Floatables (Does Not Include Trash) | Floatables Description | Other - Floatables Description | Notes | insp_type
OF_293 | 2930 | CB | Tadmuck Lane | 2021-10-07 15:42 | Sam_Downes | 65 | 1.6 | 0.0 |  |  | No |  | Yes | Trickle | Both directions. | No | 0.25 | 0.0 | 0.11 | No |  |  | No |  |  | Flow from CB 2931 | Dry Key Junction
OF_293 | 2930 | CB | Tadmuck Lane | 2021-10-07 15:42 | Sam_Downes | 65 | 1.6 | 0.0 |  |  | No |  | Yes | Trickle | Both directions. | No | 0.25 | 0.0 | 0.05 | No |  |  | No |  |  | Flow from CB 2932 | Dry Key Junction
OF_292 | 2938 | CB | Fairview Drive | 2021-10-07 17:09 | Sam_Downes | 65 | 1.6 | 0.0 |  |  | Partially | Both. | Yes | Trickle | From down street towards MH | No | 0.0 | 0.0 | 0.04 | No |  |  | No |  |  |  | Dry Key Junction
COLOR KEY (benchmarks are bold)
| Ammonia | Surfactants | Chlorine
| mg/L | mg/L | mg/L
| 6 | 1 | 1
| 1 | 0.5 | 0.3
| 0.5 | 0.25 | 0.02
| < 0.5 | < 0.25 | < 0.02
Benchmark Sources:
Ammonia, Surfactants, and Chlorine - EPA General Permit for Stormwater Discharges from Small MS4 in Massachusetts