## Added to Oufall Inventory
Outfall_ID | Location | In MS4 Area? | Receiving Water | Dry Weather Outfall Screening Status | Notes | PRIORITY RANKING | Key Junction Inspection Status | Terminal Structure Status | SVF Analysis | Wet Weather Screening Status
New4.26_1 | 42 E. Prescott | Yes | Outside Receiving | Completed | Located in PY6 | Low | No KJ | Not confirmed
New4.26_2A | Misty Lane | Yes | Outside Receiving | Completed | Located in PY6 | Low
New4.26_2B | Misty Lane | Yes | Outside Receiving | Completed | Located in PY6 | Low | Complete | Confirmed
New4.26_3 | 6 Deer Run Drive | Yes | Outside Receiving | Completed | Located in PY6 | Low |  |  | No SVFs | N/A
New4.26_4 | 8 Deer Run Drive | Yes | Outside Receiving | Completed | Located in PY6 | Low |  |  | No SVFs | N/A
New4.26_5 | 6 Baldwin Rd | Yes | Outside Receiving | Completed | Located in PY6 | Low
New4.26_6 | 30 North St | Yes | Outside Receiving | Completed | Located in PY6 | Low
New4.24 | Magnolia Dr near Greenbier Dr | Yes | Outside Receiving | Not Screened | Located in PY6 | To be determined |  |  | Yes SVFs | Not screened
New5.13 | 34 Kirsi Circle | Yes | Outside Receiving | Not Screened | Located in PY6 | To be determined
New5.21 | 8 Crest Dr | Yes | Outside Receiving | Completed | Located in PY6 | Low

## Outfall Sampling Results
Location |  |  |  |  | Laboratory Analysis (1) |  |  |  |  | Water Quality Meter/Test Kit (1)
Date | Time | Outfall ID | Street | Sample Location | Ammonia | Surfactants | E. coli | Total Phosphorus | Temperature | Temperature | Salinity | Conductivity | Chlorine | Ammonia | Dissolved Oxygen
|  |  |  | (Outfall / Upstream MH) | mg/L | mg/L | CFU/100mL | mg/L | oC | oF | ppt | µS/cm (2) | mg/L | mg/L | mg/L
2024-04-26 | 10:17 | New4.26_1 | 42 East Prescott | Outfall | 0.104 | ND | ND | - | 10.4 | 50.72 | 0.1 | 145.2 | 0 | 0 | -
2024-04-26 16:00 | 10:49 | New4.26_6 | 30 North Street | Outfall | 0.135 | ND | ND | - | 8.8 | 47.84 | 0.27 | 388.4 | 0.09 | 0.5 | -
2024-04-26 16:00 | 11:36 | New4.26_3 | 6 Deer Run Drive | Upstream DMH-2668 | 0.704 | ND | 11 | - | 12.6 | 54.68 | 0.24 | 369.9 | 0.06 | 0.25 | -
2024-04-26 16:00 | 12:01 | New4.26_4 | 8 Deer Run Drive | Outfall | ND | ND | 5 | - | 11.6 | 52.88 | 0.14 | 212.3 | 0.05 | 0 | -
REPORTING LIMITS Ammonia = 0.075 mg/L Surfactants = 0.050 mg/L E. coli = 2 CFU/100mL Fecal Coliform = 2 CFU/100mL BOD5 = 2 mg/L Total Phosphorus = 0.01 mg/L "ND" = none detected |  |  |  | COLOR KEY (benchmarks are bold)
[5 empty] | Ammonia | Surfactants | E. coli | Total Phosphorus |  | Temperature | Salinity | Conductivity | Chlorine | Ammonia | Dissolved Oxygen
[5 empty] | mg/L | mg/L | CFU/100 mL | mg/L |  | oF | ppt | µS/cm | mg/L | mg/L | mg/L
[5 empty] | 6 | 1 | 10000 | 0.908 |  | 83 | 1 | 2000 | 1 | 6
[5 empty] | 1 | 0.5 | 1260 | 0.466 |  | 83 | 0.75 | 1500 | 0.3 | 1
Notes for Results Summary: |  |  |  |  | 0.5 | 0.25 | 235 | 0.024 |  | 83 | 0.5 | 1000 | 0.02 | 0.5 | 5
(1) "-" means no analysis was completed |  |  |  |  | < 0.5 | < 0.25 | < 235 | < 0.024 |  | < 83 | < 0.5 | < 1,000 | < 0.02 | < 0.5 | ≥ 5.0
(2) µS/cm is equivalent to µmhos/cm
(3) analytical method 121,9213D |  |  |  | Benchmark Sources:
Ammonia, Surfactants, and Chlorine - EPA General Permit for Stormwater Discharges from Small MS4 in Massachusetts
E. coli, Temperature, and Dissolved Oxygen - 314 CMR 4.00: Massachusetts Surface Water Quality Standards
Fecal coliform - MWRA Water Quality Standards for Class B and Class SB Waters
Total Phosphorus - EPA Ambient Water Quality Criteria Recommendations for Rivers and Streams in Nutrient Ecoregion XIV
Salinity - EPA Volunteer Estuary Monitoring: A Methods Manual
Conductivity - Center for Watershed Protection Illicit discharge Detection and Elimination Guidance Manual
BOD5 has no quantitative benchmark for surface water grab samples

## Outfall Screening Inspections
ObjectID | GlobalID | CreationDate | Creator | EditDate | Editor | Outfall ID: | Location: | Investigator | Investigator Other | Today's Date | Time (24Hr) | Temperature (°F): | Rainfall Last 72 Hours (IN): | Rainfall Last 24 Hours (IN): | Photo Description | Land Use in Drainage Area | Other - Land Use in Drainage Area | SECTION 2: Outfall Description | Other - SECTION 2: Outfall Description | Outfall Shape | Other - Outfall Shape | Outfall Material | Other - Outfall Material | Diameter/Dimensions | Slope | Submerged in Water: | Upstream Structure Accessible and Inspected | Notes on Upstream Structure | Submerged in Sediment: | Pipe Condition | Other - Pipe Condition | Outlet Structure | Other - Outlet Structure | In-Stream? | Is Flow Present? | Flow Description | SECTION 3: Quantitative Characterization | Temperature | Temperature Units | Conductivity | Conductivity Units | Salinity | Salinity Units | Ammonia (mg/L) | Chlorine (greater than 0.02 mg/L) | pH | SECTION 4: Are any Physical Indicators Present in the Flow? | Is there an odor present in the flow? | Relative Odor Severity Index (1-3) | Odor Description | Other - Odor Description | Is there any color present in the flow? | Relative Color Severity Index (1-3) | Color Description | Other - Color Description | Is there any turbidity present in the flow? | Relative Turbidity Severity Index (1-3) | Are any floatables present in the flow | Relative Floatables Severity Index (1-3) | Floatables Description | Other - Floatables Description | Section 5: Are physical indicators that are not related to flow present? | Are Deposits or Stains Present? | Deposits/Stains Description | Other - Deposits/Stains Description | Deposits/Stains Comments | Is Surrounding Vegetation Present? | Vegetation Description | Surrounding Vegetation Comments | Is Abnormal Vegetation Present in Outfall? | Abnormal Vegetation Description | Abnormal Vegetation Comments | Is There Visible Erosion of Outfall? | Erodibility Description | Erodibility Comments | Is Pool Quality Poor? | Pool Quality Description | Other - Pool Quality Description | Pool Quality Description | Is Pipe Benthic Growth Present? | Benthic Growth Description | Other - Benthic Growth Description | Benthic Growth Comments | SECTION 6: Overall Outfall Characterization as an Illicit Discharge | Section 7: Data Collection | Samples Taken to Lab | Other - Samples Taken to Lab | Samples Collected From | Where were Samples Collected From? | Intermittent Flow Trap Recommended? | Surfactants Test Results | Surfactants Test Result Units | Ammonia Test Results | Ammonia Test Result Units | E. Coli Test Results | E. Coli Test Results Units | Fecal Coliform Test Results | Fecal Coliform Test Results Units | TSS Test Results | TSS Test Results Units | Turbidity Test Results | Turbidity Test Results Units | Total Phosphorus Test Results | Total Phosphorus Test Results Units | Total Nitrogen Test Results | Total Nitrogen Results Units | Other Test Results | Other Test Results Units | SECTION 8: Any Non-Illicit Discharge Concerns | Maintenance/Report Needed | Notes | x | y
178 | 9ce59d70-2c99-40d2-99cf-d717f1da3ef0 | 2024-04-26 14:40 | LaurynPatterson | 2024-05-15 20:03 | EOlsonTB | New4.26_1 | 42 East Prescott |  | Lauryn Patterson | 2024-04-26 16:00 | 10:17 | 50 | 0.01 | 0.01 |  | open_space_–_field |  | single |  | circular |  | rcp |  | 24 | moderate | no |  |  | no | cracked |  | no_outfall_protection |  | yes | yes | moderate | yes | 10.4 | celsius | 145.2 | uS/cm | 0.1 | Ppt | 0.0 | 0.0 | 7.55 | no | [14 empty] | no | [21 empty] | unlikely | yes | surfactants_,ammonia,e_coli |  | outfall | flow | no | ND | mg/l | 0.104 | mg/l | ND | col/100ml | [13 empty] | yes | Severe erosion above outfall. | -71.4833 | 42.5842
179 | 3013aec4-3ca8-4f56-9b7f-6b52caac5ad9 | 2024-04-26 15:06 | LaurynPatterson | 2024-05-15 20:04 | EOlsonTB | New4.26_6 | 30 North Street |  | Lauryn Patterson | 2024-04-26 16:00 | 10:49 | 50 | 0.01 | 0.01 |  | open_space_–_wooded |  | single |  | circular |  | rcp |  | 12 | flat | no |  |  | no | good |  | flared_end |  | no | yes | moderate | yes | 8.8 | celsius | 388.4 | uS/cm | 0.27 | Ppt | 0.5 | 0.09 | 7.29 | no | [14 empty] | no | [21 empty] | unlikely | yes | surfactants_,ammonia,e_coli |  | outfall | flow | no | ND | mg/l | 0.135 | mg/l | ND | col/100ml | [13 empty] | no |  | -71.4662 | 42.6019
180 | b64d2812-51e2-4469-a8bb-3d0f8e607510 | 2024-04-26 16:26 | LaurynPatterson | 2024-05-15 20:05 | EOlsonTB | New4.26_3 | 6 Deer Run Drive |  | Lauryn Patterson | 2024-04-26 16:00 | 11:36 | 50 | 0.01 | 0.01 | Outfall partially submerged screened upstream drain feature FW:2668 | residential |  | single |  | circular |  | rcp |  | 24 | flat | partially | yes_dmh | drainage structure FW:2668 | no | good |  | flared_end |  | no | yes | substatial | yes | 12.6 | celsius | 369.9 | uS/cm | 0.24 | Ppt | 0.25 | 0.06 | 6.29 | no | [14 empty] | no | [21 empty] | unlikely | yes | surfactants_,ammonia,e_coli |  | upstream_manhole | flow | no | ND | mg/l | 0.704 | mg/l | 11 | col/100ml | [12 empty] | Water had minor chlorine/chemical smell. No other olfactory indicators. | no |  | -71.4075 | 42.5929
181 | 5508c131-416f-4fc6-9016-5cdd6411d407 | 2024-04-26 16:27 | LaurynPatterson | 2024-05-15 20:06 | EOlsonTB | New4.26_4 | 8 Deer Run Drive |  | Lauryn patterson | 2024-04-26 16:00 | 12:01 | 55 | 0.01 | 0.01 |  | residential |  | single |  | circular |  | rcp |  | 24 | steep | no |  |  | no | good |  | other | Unknown | no | yes | substatial | yes | 11.6 | celsius | 212.3 | uS/cm | 0.14 | Ppt | 0.0 | 0.05 | 6.73 | no | [14 empty] | no | [21 empty] | unlikely | yes | surfactants_,ammonia,e_coli |  | upstream_manhole | flow | no | ND | mg/l | ND | mg/l | 5.0 | col/100ml | [13 empty] | no | CNL OF screened upstream manhole 2669. | -71.409 | 42.5932
182 | 85ac70c4-9a92-4251-a4b8-a117c78c6a07 | 2024-04-26 16:56 | LaurynPatterson | 2024-05-07 14:44 | EOlsonTB | New4.26_2A | Misty Lane |  | Lauryn Patterson | 2024-04-26 16:00 | 12:52 | 55 | 0.01 | 0.01 |  | open_space_–_wooded |  | single |  | circular |  | rcp |  | 18 | flat | no |  |  | no | good |  | flared_end |  | no | no |  | no | [9 empty] | no | [14 empty] | no | [21 empty] | unlikely | no | [24 empty] | no | Standing water in BMP. No water leaving basin into outfall pipe. | -71.4113 | 42.5576
183 | 3594ad32-793a-424c-b8ee-5328380b8832 | 2024-04-26 17:08 | LaurynPatterson | 2024-05-07 14:45 | EOlsonTB | New4.26_2B | Misty Lane |  | Lauryn Patterson | 2024-04-26 16:00 | 12:56 | 55 | 0.01 | 0.01 | Outfall was submerged, Upstream Structure is a BMP, Iinket of BMP is partially submerged (picture 2), upstream DMH checked (no flow) | open_space_–_wooded |  | single |  | circular |  | pvc |  | 8 | flat | fully | yes_dmh | Upstream Structure is a BMP, Iinket of BMP is partially submerged (picture 2), upstream DMH checked (no flow) | no | good |  | no_outfall_protection |  | no | no |  | no | [9 empty] | no | [14 empty] | no | [21 empty] | unlikely | no | [24 empty] | no |  | -71.4113 | 42.5576
185 | aeb97dad-ef51-42c4-88c4-62160fe6e435 | 2024-04-26 17:26 | LaurynPatterson | 2024-04-26 20:41 | LaurynPatterson | UNK-7 | Steeple Chase Circle |  | Lauryn Patterson | 2024-04-26 16:00 | 13:18 | 55 | 0.01 | 0.01 | CNL outlet of detention basin screened next available upstream structure DMH 4033 which was dry. Inlet of basin was submerged | residential |  | single |  | circular |  | rcp |  | 18 | moderate | fully | yes_dmh | DMH4033 | no | good |  | no_outfall_protection |  | no | no |  | no | [9 empty] | no | [14 empty] | no | [21 empty] | unlikely | no | [24 empty] | no |  | -71.4106 | 42.5609
186 | 103f40ab-d723-4c11-aba3-39c2e4132221 | 2024-04-26 17:36 | LaurynPatterson | 2024-05-03 12:52 | EOlsonTB | New4.26_5 | 6 Baldwin Rd |  | Lauryn Patterson | 2024-04-26 16:00 | 13:33 | 55 | 0.01 | 0.01 | Screened upstream manhole 2679. Outfall on privat road / not town owned property. | residential |  | single |  | circular |  | rcp |  | 12 | flat | no |  |  | no | good |  | other | Unknown | no | no |  | no | [9 empty] | no | [14 empty] | no | [21 empty] | unlikely | no | [24 empty] | no |  | -71.406 | 42.5981
187 | 08cde402-7aaa-4abf-9a8a-5002169f22a4 | 2024-05-23 12:16 | LaurynPatterson | 2024-05-28 12:10 | EOlsonTB | New5.21 | 8 Crest Drive |  | Lauryn Patterson | 2024-05-21 16:00 | 13:07 | 87 | 0.09 | 0 |  | residential |  | single |  | circular |  | rcp |  | 12 | moderate | partially |  |  | partially | good |  | flared_end |  | no | no |  | no | [9 empty] | no | [14 empty] | no | [21 empty] | unlikely | no | [24 empty] | no |  | -71.434 | 42.5941